June 18, 2026

Ms. Sabina Arutyunyan | Kovitz Shifrin Nesbit

One Overlook Point, Suite 590

Lincolnshire, IL 60069-4331	via email: SArutyunyan@ksnlaw.com

Re: 1426 North Orleans Street Chicago, IL

Roof and Masonry Issues Dear Ms. Arutyunyyan:

The construction of the Cheval Club Condominium was completed in circa 2000-2001. The roof system installed at that time was a single layer of modified bitumen. Due to apparent use of the roof during construction, a second layer of modified bitumen roofing was installed over the initial one.

Without insulation above the concrete roof deck, water vapor from the interior condensed below the concrete roof deck on structural steel. This condensate water resulted in wet spots on the sixth floor ceiling, blisters within the paint and interior leaking.

Moisture intrusion at the perimeter walls was also experienced, apparently related to deficient masonry construction. It was with these conditions needing remediation that the Board hired Kipcon Great Lakes, LLC (Kipcon).

[HOA Comment: Can we insert a background section for any “new” readers”]

General Background Provided by the HOA

During the winter of 2025, the Board interviewed engineering firms recommended by the HOA’s management company to oversee the request for proposal process, selection of vendor, and general oversight of the project.  The Board hired Kipon Midwest Great Lakes, LLC (“Kipcon”).   Kipcon performed an initial roof and masonry inspection, prepared the request for proposal and bid documents, reviewed vendor proposals and recommended the final vendor – Ready Home, Inc. (“Ready Home”).  Kipcon prepared two separate contracts for the roofing and masonry project that were signed by Ready Home, Inc. and the Board.

Ready Home performed the roof and masonry services in October and November 2025.   During this period, Ready Home Inc, was verbally engaged to perform additional tuckpointing on the east building wall (street side).  The project was paused in November 2025 due to winter weather.   At this time, the HOA’s was told that only outstanding roof and masonry work was the implementation of the rooftop deck railing separating the private deck sections.  During the winter of 2026, a two roof leaks occurred entering the units.

# Documents Reviewed

January 2024, Kipcon Proposal:

The Kipcon proposal defines what they intend to provide to the board. The following summarizes those services:

Inspection:

- Provide a visual observation of the roof.

- Provide written report.

Comment: No written report has been produced. How can a roof be inspected when it is obscured by and us located under wood tiles is unknown

[HOA Comment:Kipcon did provide an initial inspection report.   Please see email attachments 1) inspection report, 2) Email with photos, and 3) Email confirming need for capstone flashing]  .

Specifications:

- Used the report to prepare a specification to solicit bids.

  - Product procedures.

  - Drawings to depict the work.

  - A step-by-step guide for the project.

- Not to be a book specification…Per Kipcon, not necessary.

- Prepare a site plan depicting the existing conditions.

- No invasive testing will be provided.

Comment: The scope of work is poor for a roof of this complexity. No drawings were produced and the lack of any invasive examination is very concerning.

HOA Comment: For masonry, Kipcon did to complete masonry drilling to verify flashing on capstones.  For the roof, the HOA did allow prospective roofers to do core samples.

Bidding:

- Solicitation of bids.

Comments: No pre-bid meeting was undertaken to review in person the project scope and requirements with the contractors.

Contract Administration:

- Site visits with handwritten daily reports.

- Interim punch list.

- Final punch list.

Comments: The number of site visits is not defined but given the plural use of visits, it can be assume more than the one site visit the Board is aware of.

No interim or final punch lists have been produced.

HOA Comment:  Technically, Kipcon did prepare a punchlist in Spring of 2026.   However, this punchlist was prepared by Andy with known open or unfinished tasks.   For example, Ryan’s balcony deck sealant needed to be reapplied because the sealant was flaking.    However, I’m not aware of any punchlist items prepared by Kipcon with regards to a review of Ready Homes worksmanship.  For example, I’m not aware that Kipcon did on onsite vist to ensure the work meet the contract specifications.

Kipcon’s proposal to the Board is minimal and lacks detail that professionals in the building envelope industry would expect. The Board is not composed of construction knowledgeable members and relied on Kipcon to provide services to accomplish their goals. Not only is the proposal lacking in detail, it did not provide all the services mentioned.

Pursuant to your request, I have inspected the roof at 1426 North Orleans Street, reviewed various documents and photos and discussed concerns with Mr. Mechavich and Mr. Link.

Hutchinson Design Group, Ltd.

Resilient Building Envelope Design Leadership for our Future

Following is a discussion of the bid specifications, the contract and my observations: March 2025 Preliminary Bid Documents:

Kipcon prepared a specification for the roofing removal and replacement and select masonry restoration, no drawings were prepared. From the Preliminary Bid Documents dated March 2025, the following scope of work overview was required:

- Tear-off and replacement of the existing main roof membrane, penthouse roof and north stairwell roof.

- Tear-off and replacement of the existing roof membranes located in the four (4) light wells and other minor secondary roofing areas.

- Repairs and re-flashings to the existing capstones on the parapet wall.

- Re-Flashing/Repairs (lintels if needed) to the sixth floor balcony doors.

- Re-flashing repairs to a number of windows (lintels if needed) that will be identified.

- Replacement of the existing rooftop deck and railings for the private roof decks.

- Implementation of a safety railing around the perimeter of the building

Kipcon notes the floor plan drawings are available for review and that they strongly recommend that the (contractors) visit the construction areas and obtain their own measurements.

Comment:

- No roof plans or elevations were provided that would have defined the areas of work.

- No details were provided that were required for conditions such as the door, windowsills, balustrades and side walls. The detailing of these conditions were not describe in the preliminary specifications.

- A preconstruction meeting where Kipcon could have reviewed the project with the prospective bidders was not performed.

# Specific Base Contract Work – Roofing

This specification alters the preliminary bid specifications significantly. It does not appear that the project was rebid after these changes.

Pertinent requirements delineated:

- Demolition:

  - After removal of the rooftop decks, the contractor and Kipcon shall do a complete inspection of the roof membrane to determine if any existing conditions not included in the specification will require revisions.

Hutchinson Design Group, Ltd.

Resilient Building Envelope Design Leadership for our Future

Comment: It is unknown whether this meeting took place and if a test core was taken. Conditions such a door, windowsill and roof drain details would have been reviewed: Both conditions have become problematic and are a revision to the scope of work.

  - Existing Roof Membrane:  Remove the existing roof membrane/roofing system

…to expose the concrete roof deck.

Comment: The concrete roof deck was not exposed and thus an inspection of the concrete condition was not performed. This non-compliance was never noted by Kipcon or communicated to the Board. A roof core is typically taken by the designer (Kipcon) so that the new roof system can be properly designed; or bidding contractors prior to bid so that they know what the existing conditions are for labor and dumpster determinations. Had Kipcon taken a core, they would have known that the concrete roof deck would need to be scarified to remove all the residual roofing.

Test cuts by one of the bidding contractors found water below the roofing (see photo 31). This water appears to be from condensation as a result of the lack of insulation above the roof deck. The presence of water only reinforces the need to remove the existing roofing and dry the concrete roof slab.

  - Two (2) layers of 2.6 inch insulation was to be installed.

Comment: No definition of how the insulation was to be secured is given. [Note: It appears that contractor provided proposals based on a Preliminary Specification then an updated Specification provided with the contract. In the specification within the contract, the insulation is to be mechanically fastened to the concrete roof deck]. Only one layer of insulation was installed with no deduct change order or notification to the owner provided, even though the contract provision is clear that ‘NO DEVIATION FROM THE SPECIFICATIONS SHALL BE ALLOWED WITHOUT THE WRITTEN AUTHORIZATION OF THE OWNER AS EVIDENCED BY A WRITTEN AMENDMENT TO THIS AGREEMENT (July

17, 2025, Specification for Roof Replacement (Contract between Ready Home, Inc. and Cheval Club Condominium Association) 3.0 General Conditions C. 1) was not followed.

  - In the Preliminary bid specifications, a vapor retarder is to be installed.	This requirement was deleted in the revised specifications.

Comment: The revised specifications do not require this. It is unknown whether this cost was included in the initial bid and then removed for the contract amount or left in.

Hutchinson Design Group, Ltd.

Resilient Building Envelope Design Leadership for our Future

  - Cant strips were to be installed at walls and curbs.

Comment: These do not appear to have been installed.

  - The preliminary bid specifications required that a two-ply modified bitumen roof system was to be installed: Base sheet and cap sheet.

    - The Contract specification reduced this to one ply.

Comment: The contract specification indicates only a one-ply. While a substantial reduction in robustness, it is unknown whether or not the original bid included two plies and if this cost was reduced or if the full cost was included in the contract.

  - All base flashings to be secured with a compression style surface-mounted counter flashing.

Comment: This was not performed.

  - Install counter flashing at all flashed conditions.

Comments: This was not performed.

  - Air Condition Condenser Units:	They are not addressed in the Preliminary Specifications but are in the Contract Specifications.

Comment: When was this cost added? It is unknown if the A/Cs were disconnected and the freon recaptured.

HOA Comment: The AC units were disconnected and reconnected.   Freon was reused.   The AC cost was included in the price.  (Post installation and AC testing, HOA identified that 1 AC unit was not recharged with freon and 1 AC unit's wiring was not connected.

  - Other:

How the various rooftop conditions are to be addressed, such as at the doors, windowsills, balustrade, high walls and at masonry walls is not addressed. At masonry walls if weeps are present is not noted? New or reuse of the existing roof edge sheet metal is not noted.

# Specific Base Contract Work – Masonry

Parapet Walls and Decorative Columns:

- Coping stone, decorative sphere, and decorative columns (balustrades) to be removed to install new through wall flashing.

Comment: The decorative columns were not lifted and no through wall flashing installed, no credit provided.

Hutchinson Design Group, Ltd.

Resilient Building Envelope Design Leadership for our Future

Lintels:

- Remove and replace the sixth floor window lintels.

Comments: This was not performed and no credit was provided.

- New through wall flashing to be installed above the sixth floor windows to be installed.

Comment: WAS THIS COMPLETED?

Tuckpointing:

- Spot pointing below the limestone to the sixth floor balconies.

Comment: Who defined the areas to be spot pointed? Observations indicate that the roof side and exterior side required 100% pointing. No water repellent was specified.

# PRICING INFORMATION

Cost on various components are listed. Costs are typically not indicated like this in a specification. Not sure of the purpose of these costs and why they are here in the Preliminary Bid Documents.

[HOA Comment:   I’ve attached a “blank” bid that was sent to the prospective roofers.   The prior bid document was a roofer’s proposal.]

Comment on the Preliminary Bid Documents

The preliminary documents are extremely loose and lack definition and clarity. The lack of corresponding drawings to define the work and details to show what is required leads to confusion and what appears to be a running list of scope reductions, without the owner’s knowledge, consent or approved deduct change order.

No new sheet metal called out. No shop drawings.

No insurance requirement in Preliminary Bid Documents. No overflows.

On-site Observations:

On Wednesday, June 3, 2026, I performed a visual observation of the roofing and masonry work at 1426 North Orleans Street (see photo 1). The purpose of the inspection was to determine if the roofing had been installed to code, manufacturer’s requirements and industry standards.

Hutchinson Design Group, Ltd.

Resilient Building Envelope Design Leadership for our Future

On the eastern half, the wood pavers had been removed and revealed the granule surfaced modified bitumen roof (see photo 2).

The following observations were made:

- The roof base flashing has been extended over the bed joint of the balustrade and a termination bar installed (see photo 3).

  - Covering the bed joint will allow water intrusion from the exposed bed joint on the opposite side.

  - A new through wall flashing was to be installed and was not.

- The base flashing extending up the brick may be covering through wall flashing and weep holes (see photo 3).

  - Verification of this will require destructive examination.

- The base flashing was extended up the concrete masonry units (CMU) wall and terminated (see photo 3). The termination bar is to be per the manufacturer’s requirements and covered with a counter flashing.

- The base flashing membrane is not well adhered below the balustrade (see photo 4).

- Metal wall siding does not appear to have been removed to terminate the top of the base flashing (see photo 5).

- Roof Drains: These were to be removed and replaced. This can only be performed with interior access and opening up of the drywall ceilings. It does not appear that this occurred.

  - The modified bitumen membrane has been inappropriately installed (see photo 6).

  - Some roof drains do not have any clamp ring bolts (see photo 6).

- The base flashing at the door sills is not appropriately terminated.

- The metal flashing below the doors does not appear to have been removed to extended the base flashing up to the door (see detail 8).

- On the east side of the roof, two roof drains were replaced apparently due to clogging and resulted in water intrusion into the roof system (see photo 9).

  - Had the roof membrane been appropriately installed at the drain when the drain backed up, water intrusion would not have resulted.

- Recent roof review by the installing contractor found open laps and patched them (see photo 10).

- Pourable sealer pockets had piping that was not separated prior to placement of the pourable sealer (see photo 11).

Hutchinson Design Group, Ltd.

Resilient Building Envelope Design Leadership for our Future

- Core cuts taken on the west side of the main roof were found wet (see photo 12).

- Stair Penthouse:

  - The roof edge base flashing is not adhered (see photo 13).

  - The gutter was not removed and is not appropriately flashed with the roofing membrane (see photo 14).

  - The coping appears to have been reused and was reinstalled with bent flanges, is too small for the parapet and is bowing (see photos 15 and 16).

- Metal wall siding does not appear to have been removed to install the roof base flashing up behind and properly terminated (see photo 17).

- The limestone atop the wall to the west of the exercise roof was not lifted and through wall flashing installed (see photo 18).

  - The new base flashing stops short of the limestone coping bed joint. The untreated CMU is very porous and water will migrate in behind the membrane (see photo 18).

    - The termination bar is not protected with a counter flashing as required by the manufacturer.

- The small roof to the north of the exercise room:

  - Exhibits the same installed characteristics as the stairwell roof: Delaminated base flashing, poorly flashed gutter, reuse of metal (see photo 19).

  - It is unknown if the correct amount of insulation and roofing layers were installed.

  - The base flashing below the clerestory windows is not per the manufacturer’s

requirements (see photo 20).

- The exercise room roof:

  - Arched and the roof edge sheet metal was reused (see photo 21).

  - The roof flashing at the gutter to roof edge is open (see photo 22).

- The new metal railings are not the appropriate length requiring wood infills (see photo 23).

Masonry Observations:

- East Parapet: The roof side masonry exhibits efflorescence (see photos 7 and 24).

- The articulated decorative limestone in the center of the parapet (sphere) was not raised to install through wall flashing (see photo 25).

- The balustrades were not raised to install through wall flashing.

Hutchinson Design Group, Ltd.

Resilient Building Envelope Design Leadership for our Future

  - The new roof base flashing was extended up past the bed joint of the balustrade (see photo 4).

- The exterior east parapet at the sixth floor was spot pointed as required (see photo 26).

  - The exterior east wall at the sixth floor has deteriorated mortar joints and should have been 100% tuckpointed (see photo 27).

- Brick on the exterior side is moving outward (see photo 28).

- The brick above the south facing brick wall over the sixth floor balcony has efflorescence and deteriorated mortar joints (see photo 29).

- The sixth floor steel balcony railing is embedded in the brick. The adjacent mortar and brick are cracked (see photo 30).

Comment: Many of the concerns above could have been addressed had photos and elevation detail drawings been prepared to convey to the contractor the intended scope and if the engineer had been on-site observing the construction.

# Conclusions

The failure of this roof system and masonry restoration project started in design and bidding which did not have a clearly defined scope of work. The bid specifications are not specific enough and have no drawings, details or technical specifications for the bidding contractors to know what is required.

While the roof design was poor, it was exacerbated by poor execution of the installation of the roof system. It was not per the manufacturer’s recommendations and does not meet code. The fact that the new roof system has moisture within it, indicates a failure.

# Opinions

Based on my review of the bid documents, contracts, photos and observation of the roof and masonry, I can, with a high degree of architectural certainty, opine that:

- The engineer erred when they told the Board a book specification was not required.

- The engineer did not provide bid documents per their proposal, and not with adequate information for the reroofing and masonry restoration to be accomplished to achieve the Board’s goals.

Hutchinson Design Group, Ltd.

Resilient Building Envelope Design Leadership for our Future

- The engineer never performed a test cut on the existing roofing.

- Test cuts by bidding contractors of the existing roofing would have found water below the original roofing (see photo 31).

  - This appears to be the result of condensation that was an issue of the sixth floor unit owners.

- The bid documents did not contain any detail drawings.

- The contract specifications differ substantially from the bid specifications.

- There were no addenda prepared revising the bid specifications.

- No shop drawings were submitted to the engineer for review.

  - There is no evidence that the engineer requested them.

- The engineer did not perform regular on-site inspections.

- The engineer did not provide written reports of site visits.

- The engineer did not provide interim or final punch lists.

- The roofing contractor did not remove the original roof as required.

  - There is water below the existing roof .

  - The roofing contractor did not notify the owner that they were not removing the existing roof as required and gain their approval prior to proceeding.

- The roofing contractor did not install the required two layers of insulation.

  - The roofing contractor did not notify the owner of this deletion and gain approval prior to proceeding.

- Base flashing are debonding.

- Base flashing terminations are not appropriate.

- The new roof is allowing water intrusion.

- Test cuts into the new roof found water.

- The roof installation was poorly installed and allowed water intrusions.

- Not all the limestone copings were lifted to install through wall flashing.

- The limestone balustrade was not lifted to install through wall flashing.

- The engineer did not meet the standard of care in defining the required roof replacement

- The engineer did not observe the roof and masonry construction appropriately.

Hutchinson Design Group, Ltd.

Resilient Building Envelope Design Leadership for our Future

I reserve the right to amend my opinions should additional information be forthcoming. Sincerely,

Thomas W. Hutchinson, AIA, CSI, Fellow-IIBEC, RRC Principal, Hutchinson Design Group, Ltd.

Attachment: Photo Report – Photos 1 – 31

Hutchinson Design Group, Ltd.

Resilient Building Envelope Design Leadership for our Future